## Revision
Revison Table
Sl | Rev | Authers | Remarks
1 | Initial Draft | Icomm | UPS Parameters are not Available. Some parameters are not Avilable in the MIB File for DG.

## Radio
| Radio Parameters | Status
S.No | Slot Information | Min value(Range) | Max value(Range)
1 | Slot1_Status | 0-(Inactive) | 1- (Active) | Slot1_Status | 1 | 0
2 | Slot1_FEC | OFF -0 | ON-1 | Status | Active | Inactive
3 | Slot1_TxPower | 15 | 36
4 | Slot1_RemoteID | R1 | R6
5 | Slot1_Link | Down Link=2 | UP link=1
6 | Slot1_ChannelNo | 1 | 302 | Slot1_Link | 2 | 1
7 |  |  |  | Status | Down Link | UP link
8 | Slot Health Table | dBm | dBm
9 | rssislot | 30 | 90
10 | syncLoss | FAIL= 0 | OK=1
11 | snr | 15 | 27
12 | txpwrslot | 15 | 36
13
14 | Voltage Parameters | dBm | dBm
15 | 5v | 0v | 5v
16 | (-)5v | (-)5v | 0v
17 | 12v | 0v | 12v
18 | 49v | 0v | 49v
19

## UPS
UPS Parameters
S.No | UPS Main Paramater | Min Value | Max Value
1 | UPS Battery Status | 64 byte String
2 | UPS Ident Manufacturer
3 | UPS Ident Model
4 | UPS Ident Software Version
5 | UPS Serial Number
6
7 | UPS Est Minutes Remaining
8 | UPS BatteryCurrent | NonNegativeInteger
9 | UPS Battery Temperature
10 | UPS input Frequency
11 | UPS Input Line Bads
12 | UPS Input Voltage
13 | UPS Input Current
14 | UPS Input True Power
15 | UPS Output Source
16 | UPS Output Frequency
17 | UPS output Current
18 | UPS output Power
19 | UPS Bypass Frequency
20 | UPS Bypass Numlines
21 | UPS Bypass Voltage
22 | UPS Bypass Current
23 | UPS Bypass Power

## DG
DG Parameters
S.No | DG Main Paramater | Min Value | Max(value)
1 | Mains Frequency | 0 | 70
2 | Mains L1 Volts | 0 | 18000
3 | Mains L2 Volts | 0 | 18000
4 | Mains L3 Volts | 0 | 18000
5 | Mains L1L2 Volts | 0 | 30000
6 | Mains L2L3 Volts | 0 | 30000
7 | Mains L3L1 Volts | 0 | 30000
8 | Mains Phase L1 | 0 | 2
9 | Mains Phase L2 | 0 | 2
10 | Mains Phase L3 | 0 | 2
11 | Mains Phase Total | NA
12 | Mains Volt LL Avg | 0 | 30000
13 | Mains Volts LL Diff | 0 | 30000
14 | Mains Volts LL Max | 0 | 30000
16 | Generator Group | Min Value | Max(value)
17 | Generator Frequency | 0 | 70
18 | Generator L3 Volts | 0 | 18000
19 | Generator L1 L2 Volts | 0 | 30000
20 | Generator L3 L2 Volts | 0 | 30000
21 | Generator L3 L1 Volts | 0 | 30000
22 | Generator phase L1 | 0 | 2
23 | Generator phase L2 | 0 | 2
24 | Generator phase L3 | 0 | 2
25 | Generator phase Total | 0 | 2
26 | Generator Volt LL Avg | 0 | 30000
27 | Generator Volt LL Diff | 0 | 30000
28 | Generator Volt LL Min | 0 | 30000
29 | Generator Volt LL Max | 0 | 30000
30 | Generator Rotation | 0 | 3
32 | Engine Group | Min Value | Max(value)
33 | Engine Oil Press | 0 | 10000
34 | Engine Temp | NA
35 | Engine Charge Alt Volts | 0 | 40
36 | Engine Battery Volts | 0 | 40
37 | Engine Speed Display | 0 | 6000

## Radio Trap
Sl | Trap ID | Trap description
1 | txpllLock | Emitted when txPLL 1- lock
2 | rxpllLock | rxPLL-lock status 0 - unlock
3 | txLowPower | Transmit power low notification 1- lock
4 | syncLossSlt1 | Synchronization lost notification for slot1
5 | syncLossSlt2 | Synchronization lost notification for slot2
6 | syncLossSlt3 | Synchronization lost notification for slot3
7 | syncLossSlt4 | Synchronization lost notification for slot4
8 | syncLossSlt5 | Synchronization lost notification for slot5
9 | syncLossSlt6 | Synchronization lost notification for slot6
10 | sysVoltagesOutOfLimitminus5V | abnormal voltages minus 5V
11 | sysVoltagesOutOfLimitplu5V | abnormal voltages plus 5V
12 | sysVoltagesOutOfLimitplus30V | abnormal voltages plus 30V
13 | sysVoltagesOutOfLimitplus49V | abnormal voltages plus 49V

## UPS Trap
Sl | Trap ID | Trap description
1 | 1 | upsAlarmBatteryBad
2 | 2 | upsAlarmOnBattery
3 | 3 | upsAlarmLowBattery
4 | 4 | upsAlarmDepletedBattery
5 | 5 | upsAlarmTempBad
6 | 6 | upsAlarmInputBad
7 | 7 | upsAlarmOutputBad
8 | 8 | upsAlarmOutputOverload
9 | 9 | upsAlarmOnBypass
10 | 11 | upsAlarmOutputOffAsRequested
11 | 12 | upsAlarmUpsOffAsRequested
12 | 13 | upsAlarmChargerFailed
13 | 14 | upsAlarmUpsOutputOff
14 | 16 | upsAlarmChargerFailed
15 | 18 | upsAlarmGeneralFault
16 | 20 | upsAlarmCommunicationsLost
17 | 167 | alarmTransferswitchSourceAFailure
18 | 168 | alarmTransferswitchSourceBFailure
19 | 170 | alarmTransferswitchRedundancyLost
20 | 171 | alarmTransferswitchOutputOverload

## Switch Trap
Sl | Trap ID | Trap description
1 | 1 | Link Down
2 | 2 | Cold Start
3 | 3 | Warm Start
4 | 4 | Link UP
5 | 5 | Aunthentication failed